BLUE FRONTIER

LD-DOAS

IN-HOUSE / FIELD COMMISSIONING REPORT

| DOAS Unit: | DOAS - ____ |
| --- | --- |
| Prepared by: |  |
| Date Cx Began: |  |
| Date Cx Concluded: |  |

Document: BF.FS.Cx-001 - Commissioning Report

Blue Frontier  |  6100 Broken Sound Pkwy NW, Suite 14, Boca Raton, FL 33487

1-833-700-BLUE  |  support@bluefrontierac.com  |  www.BlueFrontierAC.com

# 1. General Information

| Project Name / Site |  |  |  |
| --- | --- | --- | --- |
| Address |  |  |  |
| Owner / Client |  |  |  |
| General Contractor |  |  |  |
| Mechanical Contractor |  |  |  |
| Controls / BAS Contractor |  |  |  |
| Cx Agent / Firm | Blue Frontier (OEM) |  |  |
| Installation Completion Date |  |  |  |
| Winterization Required? |  |  |  |

# 2. System Overview

## 2.1 Unit Identification

| Model Number |  |  |  |
| --- | --- | --- | --- |
| Serial Number |  |  |  |
| System Type | DOAS |  |  |
| Air Discharge |  |  |  |
| Primary Function |  |  |  |

## 2.2 Airflow Design

| Supply Air CFM |  |  |  |
| --- | --- | --- | --- |
| Outside Air Intake CFM |  |  |  |
| Exhaust CFM |  |  |  |
| Exhaust BL RPM |  |  |  |

## 2.3 Refrigerant Circuit

| Refrigerant Type |  |  |  |
| --- | --- | --- | --- |
| Charge (Nameplate) |  |  |  |
| Compressor Model # |  |  |  |
| Compressor Serial # |  |  |  |
| Regenerator Model # |  |  |  |
| Regenerator Serial # |  |  |  |

## 2.4 Electrical

| Voltage |  |  |  |
| --- | --- | --- | --- |
| Phase |  |  |  |
| Hertz |  |  |  |
| MCA |  |  |  |
| MOCP |  |  |  |

## 2.5 Controller / Network

| Modem Username |  |  |  |
| --- | --- | --- | --- |
| Modem Password |  |  |  |
| Modem IP Address |  |  |  |
| Controller IP Address |  |  |  |
| Firmware Version @ Startup |  |  |  |
| EC-GFX Version @ Startup |  |  |  |
| Network Name |  |  |  |
| BAS Integration Type |  |  |  |
| BACnet/IP |  |  |  |
| BACnet MS/TP |  |  |  |
| Modbus |  |  |  |

# 3. Documentation & Submittals

| Item | Y / N / NA | Notes / Details |  |
| --- | --- | --- | --- |
| Lbs. of refrigerant per tag verified? |  |  |  |
| IOM manual in document rack? |  |  |  |
| As-builts updated and in document rack? |  |  |  |
| Wiring diagram in document rack? |  |  |  |
| P&ID in document rack? |  |  |  |
| Cx checklist in document rack? |  |  |  |
| Nameplate data verified? |  |  |  |

# 4. Physical Inspection (Field Installed)

| Item | Y / N / NA | Notes / Details |  |
| --- | --- | --- | --- |
| Equipment anchored / leveled? |  |  |  |
| Clearances maintained? |  |  |  |
| Roof / pad penetrations sealed? |  |  |  |
| Drains trapped / slope verified per IOM? |  |  |  |
| Aluminum pre-filters installed? |  |  |  |
| SA filters installed? |  |  |  |
| MERV 8 - qty & size: |  |  |  |
| MERV 15 - qty & size: |  |  |  |
| Regenerator filters installed? |  |  |  |
| MERV 8 - qty & size: |  |  |  |
| DP sensors zeroed? |  |  |  |
| Dampers correctly oriented? |  |  |  |
| Access panels / gasketing intact? |  |  |  |

# 5. Piping & Ductwork

| Item | Y / N / NA | Notes / Details |  |
| --- | --- | --- | --- |
| Check valve installed at compressor discharge? |  |  |  |
| 40 oz. of oil added to refrigerant circuit? |  |  |  |
| Exterior duct double wall? |  |  |  |
| Ductwork complete / insulated? |  |  |  |
| Water piping flushed before startup? |  |  |  |
| Strainers cleaned? |  |  |  |
| Water quality report reviewed? |  |  |  |
| Water softening system required & installed? |  |  |  |
| BF water filtration installed (with isolation valves)? |  |  |  |
| Desiccant filters installed? |  |  |  |
| Mini strainer cleaned? |  |  |  |
| Condensate drain installed per IOM? |  |  |  |
| Heat trace installed and functional? |  |  |  |
| Crankcase heater ran before startup? |  |  |  |
| Duration of crankcase heater run: |  |  |  |
| Compressor temp before startup: |  |  |  |

# 6. Electrical & Safety

| Item | Y / N / NA | Notes / Details |  |
| --- | --- | --- | --- |
| LO/TO documented? |  |  |  |
| Point-to-point verification completed? |  |  |  |
| Voltage / phasing verified? |  |  |  |
| Grounding verified? |  |  |  |
| Disconnect / breaker labeled? |  |  |  |
| E-Stop tested & functional? |  |  |  |
| Smoke / CO sensors installed? |  |  |  |
| Condensate float switches tested? |  |  |  |
| Pan switches tested? |  |  |  |
| TRH sensors tested and verified? |  |  |  |
| DP sensors zeroed out? |  |  |  |
| Level sensors functional? |  |  |  |
| All blowers configured? |  |  |  |
| VFD configuration complete? |  |  |  |
| Superheat controller configured? |  |  |  |
| Power meter configured? |  |  |  |
| Speed controllers configured? |  |  |  |
| Schedules set in controller? |  |  |  |

| Technician Verification: |  | Date: |  |
| --- | --- | --- | --- |

# 7. Start-Up Checklist

| Start-Up Performed by |  |  |  |
| --- | --- | --- | --- |
| Date |  |  |  |
| Witnessed by |  |  |  |

# 8. Functional Performance Tests (FPT)

Document each of the following metrics upon startup.

## 8.1 Airside Performance

| Test | Measured | Design | Pass / Fail |
| --- | --- | --- | --- |
| Supply Airflow (CFM) |  |  |  |
| OA Airflow (CFM) |  |  |  |
| CEA Airflow (CFM) |  |  |  |
| SA RH% |  |  |  |
| Supply Air Dewpoint (°F) |  |  |  |
| Regen EA (CFM) |  |  |  |

## 8.2 Refrigeration Circuit

| Suction (psig) | Discharge (psig) | Suction T (°F) | Liquid T (°F) | SH (°F) |
| --- | --- | --- | --- | --- |

## 8.3 Desiccant

| Parameter | Value |
| --- | --- |
| Desiccant Concentration (%) |  |
| Regenerator Inlet T (°F) |  |
| Regenerator Outlet T (°F) |  |
| Desiccant Flow (LPM) |  |

## 8.4 Electrical Components

| Component | Setpoint RPM | Actual RPM | Nameplate (A) | Amp Draw |
| --- | --- | --- | --- | --- |
| C_BL1 |  |  |  |  |
| C_BL2 |  |  |  |  |
| C_BL3 |  |  |  |  |
| R_BL1 |  |  |  |  |
| Compressor |  |  |  |  |
| Heater(s) |  |  |  |  |

# 9. Controls / BAS Sequences

Mode transitions: Off → Enable → Cool → Regen → Enable/ON/OFF

## 9.1 Setpoints

| Point Name | SP | Unit State | Command / Stimulus | Observed |
| --- | --- | --- | --- | --- |
| SA_DP |  |  |  |  |
| SA_CFM |  |  |  |  |
| EA_CFM |  |  |  |  |
| LD_CONC |  |  |  |  |
| IECW_FLOW |  |  |  |  |
| DCW_FLOW |  |  |  |  |
| C_FM3 |  |  |  |  |

## 9.2 Airflow Summary

Attach full TAB report.

| Sub-System | Design CFM | Measured CFM | Delta | Damper Pos. |
| --- | --- | --- | --- | --- |
| Conditioner |  |  |  |  |
| Regenerator |  |  |  |  |

# 10. Deficiencies, Issues & Corrective Actions Log

| DEF# | Date | Description | Severity | Root Cause | Interim Fix | Final Resolution |
| --- | --- | --- | --- | --- | --- | --- |
| 01 |  |  |  |  |  |  |
| 02 |  |  |  |  |  |  |
| 03 |  |  |  |  |  |  |
| 04 |  |  |  |  |  |  |
| 05 |  |  |  |  |  |  |

# 11. Training & Turnover

| Item | Y / N / NA | Notes / Details |  |
| --- | --- | --- | --- |
| O&M training delivered to operations staff? |  |  |  |
| Attendees list attached? |  |  |  |
| Training materials provided? |  |  |  |
| Consignment inventory of spare parts turned over? |  |  |  |
| Consignment inventory list signed & attached? |  |  |  |
| PM schedule baseline provided? |  |  |  |
| Extra set of air and desiccant filters turned over? |  |  |  |

## 11.1 BMS Integration

| Item | Y / N / NA | Notes / Details |  |
| --- | --- | --- | --- |
| BMS integrated? |  |  |  |
| BMS system type: |  |  |  |
| DOAS visible to BMS? |  |  |  |
| BMS graphics verified? |  |  |  |
| Alarm list and acronyms defined? |  |  |  |

## 11.2 Monitoring & Warranty

| Blue Frontier Monitoring Period Start Date |  |  |  |
| --- | --- | --- | --- |
| Warranty Explained to Customer? |  |  |  |
| Parts Warranty Start Date |  |  |  |
| Compressor Warranty Start Date |  |  |  |

# 12. Documentation Attachments

| Item | Y / N / NA | Notes / Details |  |
| --- | --- | --- | --- |
| Approved submittals? |  |  |  |
| As-built drawings? |  |  |  |
| TAB report? |  |  |  |
| Site water analysis? |  |  |  |
| Refrigerant log / EPA record? |  |  |  |
| Leak test results (factory)? |  |  |  |
| Photos (nameplate, anchorage, duct seals, drains)? |  |  |  |
| Calibration certificates (if applicable)? |  |  |  |
| Sequence of operation (final)? |  |  |  |
| Copy of BAS point list & mapping? |  |  |  |
| Training sign-in sheets? |  |  |  |
| Factory Cx report? |  |  |  |
| Field Cx report? |  |  |  |

# 13. Sign-Off & Final Acceptance

| Item | Y / N / NA | Notes / Details |  |
| --- | --- | --- | --- |
| All deficiencies closed? |  |  |  |
| All documentation delivered? |  |  |  |
| Owner acceptance walk complete? |  |  |  |
| All permits closed? |  |  |  |
| All M&M agreements signed? |  |  |  |

## Final Acceptance Signatures

| Owner Rep: |  | Date: |  | Sign: |  |
| --- | --- | --- | --- | --- | --- |

| Cx Agent: |  | Date: |  | Sign: |  |
| --- | --- | --- | --- | --- | --- |

| Mechanical Contractor: |  | Date: |  | Sign: |  |
| --- | --- | --- | --- | --- | --- |

| Controls Contractor: |  | Date: |  | Sign: |  |
| --- | --- | --- | --- | --- | --- |

# 14. Safety & Compliance Checklist

| Item | Y / N / NA | Notes / Details |  |
| --- | --- | --- | --- |
| Lockout / Tagout observed? |  |  |  |
| Fall protection? |  |  |  |
| Refrigerant handling per EPA? |  |  |  |
| MSDS / SDS available? |  |  |  |
| Job hazard analysis reviewed? |  |  |  |
| First aid kit present? |  |  |  |

Keep this report and all attachments in the project turnover package as well as the digital file for this system in the Field Services Department.

Blue Frontier  |  6100 Broken Sound Pkwy NW, Suite 14, Boca Raton, FL 33487

1-833-700-BLUE  |  support@bluefrontierac.com  |  www.BlueFrontierAC.com